## IEEE 141 Fig 3-11
This spreadsheet calculates the value of the source voltage for a given load voltage, load current and cable impedance. This is presented according to the arrangement shown in IEEE 141 Fig 3-11. This also allows an assessment of the accuracy of the IEEE 141 simplified estimate formula. Instructions: fill in the yellow highlighted cells with your plant data
|  |  |  | Magnitude | Angle |  | Resistive | Reactive
Vload_ph-n |  |  |  | 1000 | 0 | è | 1000 | 0 |  |  | Vload 1000 V @ 0 deg | 0 | 1000
[12 empty] | 0 | 0
Iload |  |  |  | 500 | -30 | è | 433.0127 | -250 |  |  | Iload 500 A @ -30 deg | 0 | 433.0127
[12 empty] | 0 | -250
Total angle difference Iload relative to Vload θ |  |  |  |  | -30
Load Power Factor (Cosθ) |  |  |  | 0.86603
Power Factor Quadrant |  |  |  | Lagging
Reactive Factor (Sinθ) |  |  |  | -0.5
We know the line impedance from the cable data Rcable + jXcable per metre: | [6 empty] | Rcable | Xcable
[7 empty] | 0.001 | 0.0015
Length of Cable (metres) |  |  |  | 1000 |  |  | ê | ê
Total Zcable |  |  |  | 1.8028 | 56.3099 | ç | 1 | 1.5
The voltage appearing end-to-end of the cable will be Vcable =I x Z (i.e. multiply vector magnitude, add vector angles)
Vcable |  |  |  | 901.3878 | 26.3099 | è | 808.0127 | 399.5191 |  |  | Vcable 901.4 V @ 26.3 deg | 0 | 808.0127 | Iload x Zcable | 1000 | 1808.0127
[12 empty] | 0 | 399.5191 |  | 0 | 399.5191
Vsource is the sum of Vload_ph-n plus the Vcable (i.e. add the respective resistive and reactive components)
Vsource |  |  |  | 1851.6278 | 12.4605 | ç | 1808.0127 | 399.5191 |  |  | Vsource 1851.6 V @ 12.5 deg | 0 | 1808.0127
[12 empty] | 0 | 399.5191
The difference in magnitude of Vsource compared to Vload_ph-n is |  |  |  | 851.6278
The voltage magnitude end-to-end across the cable is |  |  |  | 901.3878
IEEE Formula |  |  |  | 808.0127 | i.e. 0.95 times actual Vdiff | [7 empty] | 95%
| 500 | -30 | 433.0127 | -250 |  |  |  |  | 0 | 433.0127 | Iload x Rcable | 1000 | 1433.0127
[9 empty] | 0 | -250 |  | 0 | -250
| 750 | 60 | 375 | 649.5191 |  |  |  |  | 0 | 375 | Iload x Xcable | 1433.0127 | 1808.0127
[9 empty] | 0 | 649.5191 |  | -250 | 399.5191