## Sheet1
Highlighted cells can be modified according to your system
Show voltage as : select V or kV | kV
System Voltage | 22
Frequency | 50
Show load as : select as A, kA, kW or kVA | A
Measured Load | 1000
Measured Load Power Factor (0 to +1) λ = ¦Pload¦ / ¦Sload¦ | 0.95
Measured Lagging or Leading | Lagging
System Volts | 22000 | Sload =22000 kVA , PF = 0.95 Lagging
Load Power Pload (kilo Watt) | 20900
Load Reactive Power Qload (kilo var) | 6869.4978
Load Apparent Power Sload (kilo VA) | 22000
LoadCurrent Iload (Amp) | 1000 | Ssupply = 21111 kVA, PF = 0.99 Lagging
Electricity Tarriff | 0.5
Maximum Demand Tarriff | 100
Running hours | 100 | 0 | 20900 | 0 | 0 | 20900 | 20900 | 0 | 20900 | 20900 | 20900 | 0 | 20900
Running cost | 1045000 | 0 | 0 | 0 | -3892.1968 | 0 | 6869.4978 | 0 | 6869.4978 | 0 | 2977.301 | 0 | 2977.301
Maximum Demand Charge | 2200000
Total cost | 3245000 | [5 empty] | 20900
22990
Target Supply Power Factor (0 to +1) λ = ¦Psupply¦ / ¦Ssupply¦ | 0.99
Target Lagging or Leading | Lagging
Supply Power Psupply (kilo Watt) | 20900
Supply Reactive Power Qsupply (kilo var) | 2977.301
Supply Apparent Power Ssupply (kilo VA) | 21111
Supply Current Iload + Ireact (Amp) | 959.5909
Required Reactance (-ve add capacitance, +ve remove capacitance) | -3892.1968
Capacitance | -25.5976
Running cost (based on kWh) | 1045000
Maximum Demand Charge (based on max average kVA) | 2111100
Total Cost | 3156100
Saving | 88900