## Sheet1
Highlighted cells can be modified according to your system
Version 2024-02-21
Single/Three Phase | Three Phase
Show voltage as : select V or kV | kV
System Voltage | 66
Frequency | 60
Show load as : select as A, kA, kW or kVA | kVA
Measured Load | 41800
Measured Load Power Factor (0 to +1) λ = ¦Pload¦ / ¦Sload¦ | 0.5
Measured Lagging or Leading | Lagging
System Volts | 66000 | Sload =41800 kVA , PF = 0.5 Lagging
LoadCurrent Iload (Amp) | 365.6552 | Ssupply = 21111 kVA, PF = 0.99 Lagging
Load Apparent Power Sload (kiloVA) | 41800
Load Power Pload (kiloWatt) | 20900
Load Reactive Power Qload (kilovar) | 36199.8619
Electricity Tarriff | 0.5
Maximum Demand Tarriff | 100
Running hours | 100 | 0 | 20900 | 0 | 0 | 20900 | 20900 | 0 | 20900 | 20900 | 20900 | 0 | 20900
Running cost | 1045000 | 0 | 0 | 0 | -33222.5609 | 0 | 36199.8619 | 0 | 36199.8619 | 0 | 2977.301 | 0 | 2977.301
Maximum Demand Charge | 4180000
Total cost | 5225000 | [5 empty] | 36199.8619
39819.8481
Target Supply Power Factor (0 to +1) λ = ¦Psupply¦ / ¦Ssupply¦ | 0.99
Target Lagging or Leading | Lagging
Supply Power Psupply (kilo Watt) | 20900
Supply Reactive Power Qsupply (kilo var) | 2977.301
Supply Apparent Power Ssupply (kilo VA) | 21111
Supply Current Iload + Ireact (Amp) | 319.8636
Required Reactance (-ve add capacitance, +ve remove capacitance) | -33222.5609
Capacitance | -20.2308
Running cost (based on kWh) | 1045000
Maximum Demand Charge (based on max average kVA) | 2111100
Total Cost | 3156100
Saving | 2068900