## Sheet1
Highlighted cells can be modified according to your system
Version 2024-02-21
Single/Three Phase | Single Phase
Show voltage as : select V or kV | kV
System Voltage | 66
Frequency | 50
Show load as : select as A, kA, kW or kVA | kVA
Measured Load | 41800
Measured Load Power Factor (0 to +1) λ = ¦Pload¦ / ¦Sload¦ | 0.8
Measured Lagging or Leading | Lagging
System Volts | 66000 | Sload =41800 kVA , PF = 0.8 Lagging
LoadCurrent Iload (Amp) | 633.3333 | Ssupply = 33778 kVA, PF = 0.99 Lagging
Load Apparent Power Sload (kiloVA) | 41800
Load Power Pload (kiloWatt) | 33440
Load Reactive Power Qload (kilovar) | 25080
Electricity Tarriff | 0.5
Maximum Demand Tarriff | 100
Running hours | 100 | 0 | 33440 | 0 | 0 | 33440 | 33440 | 0 | 33440 | 33440 | 33440 | 0 | 33440
Running cost | 1672000 | 0 | 0 | 0 | -20313.483 | 0 | 25080 | 0 | 25080 | 0 | 4766.517 | 0 | 4766.517
Maximum Demand Charge | 4180000
Total cost | 5852000 | [5 empty] | 33440
36784
Target Supply Power Factor (0 to +1) λ = ¦Psupply¦ / ¦Ssupply¦ | 0.99
Target Lagging or Leading | Lagging
Supply Power Psupply (kilo Watt) | 33440
Supply Reactive Power Qsupply (kilo var) | 4766.517
Supply Apparent Power Ssupply (kilo VA) | 33778
Supply Current Iload + Ireact (Amp) | 511.7879
Required Reactance (-ve add capacitance, +ve remove capacitance) | -20313.483
Capacitance | -14.8439
Running cost (based on kWh) | 1672000
Maximum Demand Charge (based on max average kVA) | 3377800
Total Cost | 5049800
Saving | 802200